{"text_format":"1","workbook":"xlsx","n_sheets":4,"sheets":["Parametere","FTA primær kjølesystem","ETA","FTA sekundær kjølesystem"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":0,"defined_names":26,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Parametere","index":0,"n_rows":12,"n_cols":8,"rows_kept":12,"cut":false,"hidden":false,"merged":[]}
["Enhet","MTTF (år)","MDT (t)","t (t)","navn","l","navn","q"]
["Pumpe, P1",1,8,null,"lambda_P1",{"$f":"1/(9760*B2)","v":1.0245901639344262E-4},"q_P1",{"$f":"C2*F2","v":8.1967213114754098E-4}]
["Pumpe, P2",1,8,null,"lambda_P2",{"$f":"1/(9760*B3)","v":1.0245901639344262E-4},"q_P2",{"$f":"C3*F3","v":8.1967213114754098E-4}]
["Elektrisk motor, M1 ",2,24,null,"lambda_M1",5.1229508196721311E-5,"q_M1",1.2295081967213114E-3]
["Elektrisk motor, M2",2,24,null,"lambda_M2",5.1229508196721311E-5,"q_M2",1.2295081967213114E-3]
["Varmeveksler, VV",4,48,null,"lambda_VV",2.5614754098360656E-5,"q_VV",1.2295081967213114E-3]
["Strømforsyning, S",5,4,null,"lambda_S",2.0491803278688525E-5,"q_S",8.1967213114754098E-5]
["Pumpe P3",5,null,730,"lambda_P3",2.0491803278688525E-5,"q_P3",{"$f":"D8*F8/2","v":7.4795081967213113E-3}]
["Dieselmotor, DM",4,null,730,"lambda_DM",2.5614754098360656E-5,"q_DM",{"$f":"D9*F9/2","v":9.3493852459016393E-3}]
["Temperaturmåler, TT",6,null,730,"lambda_TT",1.7076502732240437E-5,"q_TT",6.2329234972677595E-3]
[]
[null,null,null,null,null,"Q sjøvann",null,{"$f":"SUM(H8:H10)","v":2.3061816939890709E-2}]

{"sheet":"FTA primær kjølesystem","index":1,"n_rows":14,"n_cols":5,"rows_kept":14,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"Q0 - bidrag","Formel","F0 - bidrag","Formel"]
["Cut set(s) with 1 component"]
["   {S} ",{"$f":"q_S","v":8.1967213114754098E-5},{"$f":"ShowFormula(B5)","v":"=q_S"},{"$f":"lambda_S","v":2.0491803278688525E-5},{"$f":"ShowFormula(D5)","v":"=lambda_S"}]
["   {VV} ",{"$f":"q_VV","v":1.2295081967213114E-3},{"$f":"ShowFormula(B6)","v":"=q_VV"},{"$f":"lambda_VV","v":2.5614754098360656E-5},{"$f":"ShowFormula(D6)","v":"=lambda_VV"}]
[" ",null,"",null,""]
["Cut set(s) with 2 components ",null,"",null,""]
["   {P1,P2} ",{"$f":"q_P1*q_P2","v":6.7186240257995167E-7},"=q_P1*q_P2",{"$f":"lambda_P1*q_P2+q_P1*lambda_P2","v":1.6796560064498792E-7},"=lambda_P1*q_P2+q_P1*lambda_P2"]
["   {P1,M2} ",{"$f":"q_P1*q_M2","v":1.0077936038699273E-6},"=q_P1*q_M2",{"$f":"lambda_P1*q_M2+q_P1*lambda_M2","v":1.6796560064498789E-7},"=lambda_P1*q_M2+q_P1*lambda_M2"]
["   {M1,P2} ",{"$f":"q_M1*q_P2","v":1.0077936038699273E-6},"=q_M1*q_P2",{"$f":"lambda_M1*q_P2+q_M1*lambda_P2","v":1.6796560064498789E-7},"=lambda_M1*q_P2+q_M1*lambda_P2"]
["   {M1,M2} ",{"$f":"q_M1*q_M2","v":1.5116904058048908E-6},"=q_M1*q_M2",{"$f":"lambda_M1*q_M2+q_M1*lambda_M2","v":1.2597420048374091E-7},"=lambda_M1*q_M2+q_M1*lambda_M2"]
["Q0=",{"$f":"SUM(B5:B12)","v":1.31567454985219E-3},"F0=",{"$f":"SUM(D5:D12)","v":4.6736428379467886E-5}]
["Q0× 8760 = timer per år =",{"$f":"B13*8760","v":11.525309056705185},null,{"$f":"D13*8760","v":0.4094111126041387},"(Frekvens per år)"]

{"sheet":"ETA","index":2,"n_rows":10,"n_cols":9,"rows_kept":10,"cut":false,"hidden":false,"merged":[]}
["¯ = Nei, ® = Ja"]
[null,null,null,null,null,null,null,null,"Formel, Frekvens"]
["Ingen kjøling VV, f=",null,"SS feiler, q=",null,null,null,"Ingen kjøling, F="]
[{"$f":"F_0","v":4.6736428379467886E-5},null,{"$f":"Q0_Secondary","v":2.3061816939890709E-2},null,null,null,{"$f":"fInit*q_SS","v":1.0778269557116014E-6},null,{"$f":"ShowFormula(G4)","v":"=fInit*q_SS"}]
[{"$f":"ShowFormula(fInit)","v":"=F_0"},null,{"$f":"ShowFormula(q_TT2)","v":"=Q0_Secondary"},null,null,null,{"$f":"G4*8760","v":9.4417641320336289E-3},"år-1"]
[null,null,null,null,null,null,{"$f":"1/G5","v":105.91241064868811},"år mellom forekomst"]
[null,null,null,null,null,null,"Sjøvannskjøling, F="]
[null,null,null,null,null,null,{"$f":"fInit*(1-q_SS)","v":4.5658601423756285E-5},null,{"$f":"ShowFormula(G8)","v":"=fInit*(1-q_SS)"}]
[null,null,null,null,null,null,{"$f":"G8*8760","v":0.39996934847210508},"år-1"]
[null,null,null,null,null,null,{"$f":"1/G9","v":2.5001915867304083},"år mellom forekomst"]

{"sheet":"FTA sekundær kjølesystem","index":3,"n_rows":11,"n_cols":3,"rows_kept":11,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
["Cut set(s) with 1 component ","Q0 - bidrag","Formel"]
["   {P3} ",{"$f":"q_P3","v":7.4795081967213113E-3},{"$f":"ShowFormula(B6)","v":"=q_P3"}]
["   {DM} ",{"$f":"q_DM","v":9.3493852459016393E-3},"=q_DM"]
["   {LE} ",0,"0"]
["   {TT} ",{"$f":"q_TT","v":6.2329234972677595E-3},"=q_TT"]
["Q0=",{"$f":"SUM(B2:B9)","v":2.3061816939890709E-2},"=SUM(B2:B9)"]
["Q0× 8760 = timer per år =",{"$f":"B10*8760","v":202.02151639344262},"=B10*8760"]